## Parameters
Parameters* | Unit of Measure | Lithium-ion LFP | Lithium-ion LFP | Lithium-ion LFP | Vanadium Redox Flow | Vanadium Redox Flow | Vanadium Redox Flow | Pumped-storage Hydro
Capex | USD/kWhcap | 427.18 | 385.21 | 399.72 | 708.15 | 505.88 | 672.27 | 511
O&M | USD/kWcap-y | 2.56 | 4.27 | 2.37 | 4.44 | 6.16 | 4.24 | 28.1
Decommiss. costs | USD/kWhcap | 2.65 | 2.65 | 2.65 | 48.64 | 33.94 | 46.1 | 0
Round-trip Eff. | % | 83% | 83% | 83% | 65% | 65% | 65% | 80%
Construction time | years | 1 | 1 | 1 | 1 | 1 | 1 | 5
Project operational life | years | 20 | 20 | 20 | 24 | 24 | 24 | 60
Economic life | years | 20 | 20 | 20 | 24 | 24 | 24 | 30
DoD | % | 80% | 80% | 80% | 80% | 80% | 80% | 80%
Power Capacity | MWcap | 100 | 100 | 1000 | 100 | 100 | 1000 | 100
Duration | hours | 2 | 4 | 2 | 2 | 4 | 2 | 4
Discount factor (WACC) | % | 6.52% | 6.52% | 6.52% | 6.52% | 6.52% | 6.52% | 6.52%
* https://www.pnnl.gov/ESGC-cost-performance, described in: V Viswanathan, K Mongird, R Franks, R Baxter, "Grid Energy Storage Technology Cost and Performance Assessment", PNNL, (2022)
Computed cost values | Units | Lithium-ion LFP | Lithium-ion LFP | Lithium-ion LFP | Vanadium Redox Flow | Vanadium Redox Flow | Vanadium Redox Flow | Pumped-storage Hydro
Investment cost - CAPEX | $ | 85436000 | 154084000 | 799440000 | 141630000 | 202352000 | 1344540000 | 204400000
Fixed O&M (NPV) | $ | 2643881.1397 | 4409911.1198 | 24476555.8637 | 4989027.3375 | 6921713.6034 | 47642963.7635 | 30716714.3579
End-of-life cost (EoL) (NPV) | $ | 140676.5006 | 281353.0012 | 1406765.006 | 2005601.3707 | 2798935.4655 | 19008680.7541 | 0
Annuity at construction time | - | 0.93879 | 0.93879 | 0.93879 | 0.93879 | 0.93879 | 0.93879 | 4.1534
Annuity at end-of-economic-life | - | 11.001 | 11.001 | 11.001 | 11.9692 | 11.9692 | 11.9692 | 13.0316
Annuity at end-of-life | - | 11.2665 | 11.2665 | 11.2665 | 12.1753 | 12.1753 | 12.1753 | 15.0847
Equiv. annual Inv. + EoL + Fixed O&M costs | $/year | 8019304.0392 | 14432771.1244 | 75022407.6762 | 12417286.7797 | 17718240.4055 | 117902204.3887 | 18041983.6456
Final cost values in EURO | Units | Lithium-ion LFP | Lithium-ion LFP | Lithium-ion LFP | Vanadium Redox Flow | Vanadium Redox Flow | Vanadium Redox Flow | Pumped-storage Hydro
Avg EUR/USD year 2022 | - | 1.0538 | 1.0538 | 1.0538 | 1.0538 | 1.0538 | 1.0538 | 1.0538
Equiv. € Hourly fixed cost | €/hour | 868.7091 | 1563.4623 | 8126.9708 | 1345.1305 | 1919.3682 | 12772.021 | 1954.4384

## ESS.py
Technology | Power Capacity (MW) | Duration (h) | DoD | RTE
Lithium-ion LFP | 100 | 2 | 80% | 83% | 'Technology': | 'Lithium-ion LFP', | 'RatedPower': | 100 | , 'Duration': | 2 | , 'DoD': | 80% | , 'RTE': | 83% | 'Technology': 'Lithium-ion LFP', 'RatedPower': 100, 'Duration': 2, 'DoD': 0.8, 'RTE': 0.83
Lithium-ion LFP | 100 | 4 | 80% | 83% | 'Technology': | 'Lithium-ion LFP', | 'RatedPower': | 100 | , 'Duration': | 4 | , 'DoD': | 80% | , 'RTE': | 83% | 'Technology': 'Lithium-ion LFP', 'RatedPower': 100, 'Duration': 4, 'DoD': 0.8, 'RTE': 0.83
Lithium-ion LFP | 1000 | 2 | 80% | 83% | 'Technology': | 'Lithium-ion LFP', | 'RatedPower': | 1000 | , 'Duration': | 2 | , 'DoD': | 80% | , 'RTE': | 83% | 'Technology': 'Lithium-ion LFP', 'RatedPower': 1000, 'Duration': 2, 'DoD': 0.8, 'RTE': 0.83
Vanadium Redox Flow | 100 | 2 | 80% | 65% | 'Technology': | 'Vanadium Redox Flow', | 'RatedPower': | 100 | , 'Duration': | 2 | , 'DoD': | 80% | , 'RTE': | 65% | 'Technology': 'Vanadium Redox Flow', 'RatedPower': 100, 'Duration': 2, 'DoD': 0.8, 'RTE': 0.65
Vanadium Redox Flow | 100 | 4 | 80% | 65% | 'Technology': | 'Vanadium Redox Flow', | 'RatedPower': | 100 | , 'Duration': | 4 | , 'DoD': | 80% | , 'RTE': | 65% | 'Technology': 'Vanadium Redox Flow', 'RatedPower': 100, 'Duration': 4, 'DoD': 0.8, 'RTE': 0.65
Vanadium Redox Flow | 1000 | 2 | 80% | 65% | 'Technology': | 'Vanadium Redox Flow', | 'RatedPower': | 1000 | , 'Duration': | 2 | , 'DoD': | 80% | , 'RTE': | 65% | 'Technology': 'Vanadium Redox Flow', 'RatedPower': 1000, 'Duration': 2, 'DoD': 0.8, 'RTE': 0.65
Pumped-storage Hydro | 100 | 4 | 80% | 80% | 'Technology': | 'Pumped-storage Hydro', | 'RatedPower': | 100 | , 'Duration': | 4 | , 'DoD': | 80% | , 'RTE': | 80% | 'Technology': 'Pumped-storage Hydro', 'RatedPower': 100, 'Duration': 4, 'DoD': 0.8, 'RTE': 0.8